## Mandatory
Engineering Configuration Data Requirement Sheet — Mandatory
HAZECO. Reviewed 19 October 2026. 33 items. Required for the existing full engineering approval/export workflow.
Fill the amber Actual Value column only. Reference examples require departmental confirmation. Source keys are explained on Evidence and Scope.
Sr. No. | Parameter / Configuration Name | Purpose / Technical Description | Required Format / Unit | Sample / Possible Value | Source / Responsible Department | Actual Value (To Be Filled) | Remarks / Priority
A. Approval, template and installed equipment libraries
1 | Target SynerGEE product / version | Confirm the receiving installation can interpret the schema and equipment references. SAI_Control.Product must match the approved template. | Exact product/version text; template registry value | Reference: SynerGEE Electric 5.0.0.324 | System Planning / SynerGEE Administrator |  | Mandatory full mode. Reference version is known; actual receiving version needs confirmation. [EPB, WR]
2 | Clean approved MDB template | Provide a genuine empty network template with the approved fields, indexes and relationships, then register and approve it. | Jet MDB file; template code/version; approved registry selection | Reference structure: 50 tables, 1,065 fields, 133 indexes, 41 relationships | SynerGEE Administrator / Application Admin |  | Mandatory. Schema is available; an approved clean template and review are still required. Hash is generated by the application. [EC, WR]
3 | Installed conductor library revision | Identify the exact external library revision that resolves the conductor IDs used in the exported network. | Versioned library name/revision or controlled release identifier | Not embedded in reference MDBs | Distribution Design / SynerGEE Library Custodian |  | Mandatory approval input. An equipment ID list is not the actual conductor library. [EC, NV]
4 | Installed transformer library revision | Identify the exact external transformer library containing the approved winding, impedance and loss definitions. | Versioned library name/revision or controlled release identifier | Not embedded in reference MDBs | Transformer Engineering / Library Custodian |  | Mandatory approval input. Transformer make or kVA label does not identify a library revision. [EC, NV]
5 | Approved conductor model inventory | Provide the installed electrical definitions and literal IDs for every material/size used on an active R/Y/B/N position. | Reviewed library package plus exact ID list; native library units declared | Observed IDs: ANT, DOG, GNAT, WASP, INSULATED ANT; leading-space variants | Distribution Design / Library Custodian |  | Mandatory for conductors actually used. R/X, ratings and other model data come from the library; GPX/PDF codes do not provide them. [MDB, NV]
6 | Approved transformer model inventory | Provide installed models whose winding ratings and electrical characteristics are confirmed for the surveyed transformers. | Reviewed transformer library package and exact type IDs | Observed labels: 50 KVA, 100 KVA, 200 KVA | Transformer Engineering / Library Custodian |  | Mandatory for selected types. References contain names, not the model definitions or physical specifications. [MDB, EC]
7 | Approved line-construction model inventory | Confirm the configuration library definition is installed and suitable for the actual construction, not only that its name exists. | Exact configuration IDs and reviewed library definitions | Reference ID: 12.5/7.2 kV cross arm C2-2 | Distribution Design / Library Custodian |  | Mandatory. The voltage-looking part of an ID is not proof of the actual supply voltage. [MDB, EC, EPB]
8 | Current-project engineering approval and design basis | Confirm which historical reference conventions apply to this project and approve the completed engineering configuration. | Controlled design/review reference and authorized approval; app records user/date | Source models include historical MEPCO networks; no HAZECO engineering approval inferred | Chief Engineer / System Planning / Authorized Admin |  | Mandatory full mode. Do not manually fabricate approval IDs or dates; use the existing approval workflow. [EC, NV]
B. Coordinate reference system and supply voltages
9 | Projected CRS and zone confirmation | Select the metre-based projected CRS for the actual survey and resolve the reference-label versus coordinate discrepancy. | Projected EPSG integer; units metres; verified GPX/control-point comparison | MDB label implies EPSG:32643; GPX 591 matches EPSG:32642 within 0.46 m | GIS / Survey Department / System Planning |  | Mandatory unresolved conflict. The same point differs by about 577 km under zone 43N. Do not copy the label without GIS confirmation. [GEO, EC]
10 | CRS name matching the approved EPSG | Supply the projection name written to SAI_Control.ProjectionFile, consistent with the chosen coordinates and EPSG. | Text, maximum 255 characters in the form | Reference: WGS 1984 UTM Zone 43N; label alone is not validated | GIS / Survey Department |  | Mandatory form field. Current-project EPSG and name must agree; see CRS conflict. [EC, MDB, GEO]
11 | Operating frequency | Confirm the current-project operating frequency used by the receiving electrical models and libraries. | Numeric Hz; form accepts 50 or 60 | All nine reference control rows: 60 Hz | System Operations / System Planning |  | Mandatory. Recorded 60 Hz is source evidence, not approval for this project. [EC, MDB]
12 | Primary supply nominal voltage, line-to-line | Set the feeder nominal voltage in InstFeeders.NominalKvll and keep it consistent with the transformer supply model. | Positive numeric kV line-to-line; form maximum 1,000 kV | Reference: 11 kV; BusVoltageLevel separately 11.37 | System Planning / Grid or Distribution Operations |  | Mandatory. Do not use the separate bus operating voltage as nominal voltage without approval. [EC, EPB, MDB]
13 | LT secondary voltage, line-to-line | Provide actual LT nominal voltage. The form writes this value into InstPrimaryTransformers.SpecNomKv. | Positive numeric kV line-to-line; consistent with NomKvMode and library | Actual LT voltage unresolved. Reference stores SpecNomKv=4.16 with NomKvMode=C | Transformer Engineering / Distribution Planning |  | Mandatory unresolved input. Previous 0.4kV Data Entry export convention is not an approval for the final SynerGEE model. [EC, MDB]
C. Line construction and equipment selection
14 | Selected line configuration library ID | Select an installed, approved construction ID for the sections; the module applies its central selection to the model. | Exact case/space-sensitive reviewed ID; form maximum 200 characters | Reference: 12.5/7.2 kV cross arm C2-2 | Distribution Design / Library Custodian |  | Mandatory selection; physical applicability still requires approval. Must exist in approved template references. [EC, EPB]
15 | Phase-to-phase spacing and source-unit interpretation | Confirm actual phase spacing and the meaning of the source MUL number before it is stored in the form field labelled cm. | Positive numeric centimetres in this form; source unit interpretation confirmed | Reference raw PhaseToPhaseSpacing_MUL=121.9 | Distribution Design / SynerGEE Administrator |  | Mandatory form input. Source declares Metric globally but gives no field-level unit annotation. No conversion assumed. [EC, MDB]
16 | Phase-to-neutral spacing and source-unit interpretation | Confirm the spacing used for neutral/phase construction and its unit interpretation in the selected configuration. | Positive numeric centimetres in this form | Reference raw PhaseToNeutralSpacing_MUL=91.4 | Distribution Design / SynerGEE Administrator |  | Mandatory form input; construction applicability and units need confirmation. [EC, MDB]
17 | Average conductor height above ground | Provide the design height used by the line model; do not substitute a pole length without an approved interpretation. | Positive numeric metres; form maximum 200 m | Reference AveHeightAboveGround_MUL=9.1 under Metric convention | Distribution Design / Survey Department |  | Mandatory form input. Reference model height is available; surveyed pole height is a different quantity. [EC, MDB]
18 | Survey pole-height unit confirmation | Confirm how original handwritten heights and older records are interpreted, so height conversions are consistent. | ft or m; current new PDF entries are stored in ft | Current application entry policy: feet; MDB model height does not prove paper-form units | Survey Department / Data Verification |  | Mandatory form choice. Confirm legacy/source units separately; retain original observations. [EC, PDF, UI]
19 | Transformer supply conductor library ID | Select the approved supply conductor model and settle its exact identity in the installed library. | Exact conductor ID in approved template reference inventory | Supply R/B: DOG; Y: one leading space plus DOG | Distribution Design / Library Custodian |  | Mandatory form selection. Resolve literal aliases rather than silently trimming source IDs. [EC, MDB]
20 | Transformer secondary-link conductor library ID | Select the installed conductor for the modeled secondary link, separately from distribution span materials. | Exact conductor ID in approved template reference inventory | Link R/B: ANT; Y: one leading space plus ANT | Distribution Design / Library Custodian |  | Mandatory form selection. This family choice does not resolve the blank link neutral. [EC, MDB]
21 | Surveyed kVA capacity to approved transformer type | Provide a type selection for every capacity present in the current survey; confirm the type represents the actual equipment. | JSON object: positive kVA capacity keys mapped to exact library IDs | Candidate labels only: {"50":"50 KVA","100":"100 KVA","200":"200 KVA"} | Transformer Engineering / Library Custodian |  | Mandatory mapping. Label-derived candidates need library confirmation; add any additional surveyed capacities through reviewed models. [EC, EPB]
22 | Transformer impedance source mode | Choose whether SynerGEE uses the approved library model or explicit instance impedance values. | UseInstanceImpedance integer: 0 for library, 1 for instance values | All nine transformer instances: UseInstanceImpedance=0 | Transformer Engineering / System Planning |  | Mandatory explicit mode. Recorded PercentImpedance=0 / PercentResistance=0 are not physical zero-impedance evidence. [EC, EPB, MDB]
D. Survey interpretation and load-method decisions
23 | Two-digit survey-year interpretation window | Define how DDMMYY dates in complete waypoint IDs resolve to four-digit years. | Integer starting year; form range 1800-9900 | No source policy. A start of 2000 would interpret 00-99 as 2000-2099 | Survey Department / Data Verification |  | Mandatory form choice. This is an explanatory policy example, not an approved value; model years 2015-2025 do not establish it. [EC]
24 | Approved load-demand method | Choose measured/verified per-phase demand or a centrally approved category-rate estimation method. | manual or category_rates | No approved method recovered; 341 of 350 positive phase records are near 3 kVA/customer | System Planning / Load Research / Commercial |  | Mandatory method decision. Nine phase records differ; every positive-kVA phase has zero kW/kvar in references. [EC, MDB]
25 | Blank consumer-cell interpretation for final generation | Confirm whether a blank means unresolved information or an explicitly approved zero under the selected final-generation method. | Boolean blank_consumers_zero: false or true, with review basis | PDFs contain blanks; final-generation approval is not recorded in MDBs | Commercial / Data Verification / System Planning |  | Mandatory explicit policy. Independent Data Entry MDB zero-filling does not approve this final-model policy. [EC, NV]
26 | Demand methodology and allocation approval reference | Document the demand basis and allocation rule so section loads are reproducible and reviewed. | Text evidence, form maximum 4,000 characters; authorized review | References use fractional equal customer equivalents; app category method balances whole customers R/Y/B | System Planning / Load Research |  | Mandatory. Counts alone are not demand; source fractional allocation must not be copied as an approved integer allocation. [EC, NV]
E. Current network source and transformer connection mapping
27 | Approved source-node and terminal mapping | Specify current feeder/transformer connection aliases and bind physical source nodes to verified current survey coordinates. | mapping.networks[code].source_nodes list; unique aliases and valid waypoint links | References show feeder, HV and LV model nodes; no current-project binding approval | GIS / Distribution Planning / Survey Verification |  | Mandatory full model per transformer. GPX locates points; it does not establish the electrical source or synthetic terminal geometry. [EPB, NV]
28 | Approved source sections and explicit lengths | Define the source-to-transformer and secondary-link edges, phases, conductor IDs and modeling lengths. | source_sections list; valid from/to aliases; SectionLength_MUL in metres, nonnegative | Reference supply/link lengths: 1 m with one-unit node offsets | Distribution Planning / Network Studies |  | Mandatory full model. Historical one-metre links are modeling examples, not surveyed current lengths. [EPB]
29 | Feeder-source alias selection | Choose which source node is the feeder origin for connectivity checks and feeder creation. | feeder_node: exact alias from current source_nodes | Historical source alias/name varies by reference feeder | Distribution Planning / GIS |  | Mandatory per-transformer source mapping. Final database node IDs are generated by the application, not supplied manually. [EPB]
30 | Primary transformer section selection | Identify the approved source section on which the transformer instance must be attached. | transformer_section: exact key from source_sections | Reference transformer is attached to its first supply section | Transformer Engineering / Distribution Planning |  | Mandatory. Must resolve to an approved current section; do not copy historical section IDs. [EPB]
31 | Source-section phase and conductor schedule | Provide the exact R/Y/B/N positions on each modeled source/link edge, including absent phases. | SectionPhases fixed slots; e.g. RYB, RYBN, R BN; separate conductor IDs | Supply: RYB; secondary link: RYBN in references | Distribution Design / Network Verification |  | Mandatory for full source-section validation. An active N requires an actual approved neutral ID. [EPB]
32 | Current substation identifier in feeder mapping | Confirm the current substation identity used by the source-feeder mapping; historical names are not current identifiers. | Nonblank SubstationId string within canonical MDB field size | Historical example: 132 KVA K.Wala; not a current HAZECO assignment | Operations / Asset Register / GIS |  | Mandatory nonblank identifier. PDF headers help identify assets; official mapping requires verification. [EPB, PDF]
33 | Reviewed mapping version and current-network wiring | Review reusable table values and complete the per-transformer wiring in the existing supported mapping contract. | synergee-reviewed-v1 or v2; explicit supported table dictionaries; current networks object | 133 common technical observations; no approved current-network source wiring | Network Studies / SynerGEE Administrator / Application Admin |  | Mandatory full mode. v2 is required when exporting supported meter/PV records. Approval metadata is recorded by the application. [EC, EPB, SM]

## Conditional
Engineering Configuration Data Requirement Sheet — Conditional
HAZECO. Reviewed 19 October 2026. 62 items. Required only when the stated demand method, device or data condition applies.
Fill the amber Actual Value column only. Reference examples require departmental confirmation. Source keys are explained on Evidence and Scope.
Sr. No. | Parameter / Configuration Name | Purpose / Technical Description | Required Format / Unit | Sample / Possible Value | Source / Responsible Department | Actual Value (To Be Filled) | Remarks / Priority
F. Conditional resolution of survey and library ambiguities
34 | Exact conductor IDs for unmatched PDF materials | Resolve a printed or handwritten material to the installed conductor model only when that material is actually used. | Per-material exact ID crosswalk and technical library definition | PDF legend includes PVC variants and ABC 50/95 mm²; nine-reference IDs do not resolve all of them | Distribution Design / Library Custodian |  | Conditional on material occurrence. Do not map PVC or ABC to ANT only because that reference exists. [PDF, LOOKUP, MDB]
35 | Whitespace and alias approval for conductor IDs | Decide whether literal leading-space references are aliases or distinct entries in the receiving library. | Reviewed mapping of exact strings; preserve spaces until confirmed | Observed: ANT / " ANT", DOG / " DOG", GNAT / " GNAT", WASP / " WASP" | Library Custodian / SynerGEE Administrator |  | Conditional where affected IDs are used; all four families have reported reference variants. [MDB]
36 | Secondary-link neutral model and continuity | Resolve the neutral conductor and connection when the link is declared to carry N. | Approved NeutralConductorId and confirmed phase/neutral schedule | Reference link SectionPhases=RYBN but NeutralConductorId is blank | Distribution Design / Operations |  | Conditional on N being declared. Full section validation rejects an active N without a reviewed conductor reference. [EPB, MDB]
37 | Historic first-S / KMZ root coordinates | Provide verified historic root coordinates where the first S reference is absent from the selected GPX. | Verified latitude/longitude and source evidence; current source association | PDFs contain historic transformer references separate from new GPS sequences | GIS / Asset Survey / Data Verification |  | Conditional on unmatched historic root. The first S KMZ reference cannot be replaced by a same-number unrelated GPX point. [NV, PDF]
38 | Ambiguous or repeated waypoint identity resolution | Confirm complete group/date/GPS identity and source selection where names or repeated observations do not uniquely identify a point. | Complete text identifier, selected GPX source and verified coordinate binding | GPX labels alone do not encode an approved electrical association | Survey / GIS / Data Verification |  | Conditional on ambiguity or missing matches; keep leading zeros in text IDs. [NV, GPX]
39 | Branch, intersection and normally-open connection resolution | Confirm which observed points are electrically connected when paper intersection flags or a branched layout are ambiguous. | Verified S/E edge schedule and radial source-connected topology | PDF Int flags exist; legacy Angle/Tap_Pole/End_Type equivalence is unconfirmed | Distribution Operations / Network Studies |  | Conditional on ambiguity/loops. Current exporter rejects cycles; it does not infer electrical connectivity from Int or proximity. [NV, EPB, PDF]
40 | Route geometry or measured span length | Supply route vertices or an approved measured length when straight endpoint distance is insufficient for the modeled section. | geometry coordinate list, or positive measured_length_m in metres | Source section lengths may match endpoint distances; GPX waypoints do not always define the route | GIS / Survey / Distribution Design |  | Conditional override. A measured length requires reason, provenance and verifier approval; no additional fixed length is assumed. [NV, EPB]
41 | Coordinate correction and approval | Confirm corrected coordinates and the reason when a recorded GPX point is wrong or missing. | Finite latitude/longitude within geographic bounds; reason and authorized approval | No universal correction can be derived from a reference model | GIS / Survey Verification |  | Conditional on correction. Preserve original coordinates; approval is required before the corrected point is used. [NV, EPB]
42 | Additional capacities / mixed construction models | Provide models and a mapping approach for surveyed capacities or constructions not represented by the consolidated library. | Exact new reviewed type/configuration IDs and per-network mapping where supported | Nine files only establish 50/100/200 KVA type labels and one configuration ID | Transformer Engineering / Distribution Design / Software Team |  | Conditional on occurrence. Central settings currently apply one configuration; heterogeneous construction may need explicit mapping review. [EC, EPB]
G. Category-rate demand inputs (only when category_rates is selected)
43 | RS demand rate (1-phase residential) | Provide the approved per-customer apparent-demand rate used to convert the verified category count into estimated demand. | Numeric kVA/consumer, 0 to 1,000,000; supported rate input | No category-specific rate in MDBs; aggregate ratios include about 3, 3.8667, 4 and 5 | Load Research / Commercial / System Planning |  | Conditional: category_rates mode requires a rate for every category, including RS. Aggregate historical ratios are not an approved rate schedule. [EC]
44 | RS lagging power factor | Provide the approved factor used to calculate kW and kvar from the category apparent-demand estimate. | Numeric factor greater than 0 and at most 1; lagging model in current automatic method | No usable value: reference positive kVA has zero kW and kvar | Load Research / Metering / System Planning |  | Conditional: category_rates requires PF for RS. Signed measured kvar or another allocation method uses the verified-demand workflow. [EC, NV]
45 | RL demand rate (3-phase residential) | Provide the approved per-customer apparent-demand rate used to convert the verified category count into estimated demand. | Numeric kVA/consumer, 0 to 1,000,000; supported rate input | No category-specific rate in MDBs; aggregate ratios include about 3, 3.8667, 4 and 5 | Load Research / Commercial / System Planning |  | Conditional: category_rates mode requires a rate for every category, including RL. Aggregate historical ratios are not an approved rate schedule. [EC]
46 | RL lagging power factor | Provide the approved factor used to calculate kW and kvar from the category apparent-demand estimate. | Numeric factor greater than 0 and at most 1; lagging model in current automatic method | No usable value: reference positive kVA has zero kW and kvar | Load Research / Metering / System Planning |  | Conditional: category_rates requires PF for RL. Signed measured kvar or another allocation method uses the verified-demand workflow. [EC, NV]
47 | SC demand rate (1-phase commercial) | Provide the approved per-customer apparent-demand rate used to convert the verified category count into estimated demand. | Numeric kVA/consumer, 0 to 1,000,000; supported rate input | No category-specific rate in MDBs; aggregate ratios include about 3, 3.8667, 4 and 5 | Load Research / Commercial / System Planning |  | Conditional: category_rates mode requires a rate for every category, including SC. Aggregate historical ratios are not an approved rate schedule. [EC]
48 | SC lagging power factor | Provide the approved factor used to calculate kW and kvar from the category apparent-demand estimate. | Numeric factor greater than 0 and at most 1; lagging model in current automatic method | No usable value: reference positive kVA has zero kW and kvar | Load Research / Metering / System Planning |  | Conditional: category_rates requires PF for SC. Signed measured kvar or another allocation method uses the verified-demand workflow. [EC, NV]
49 | LC demand rate (commercial LC; classification needs confirmation) | Provide the approved per-customer apparent-demand rate used to convert the verified category count into estimated demand. | Numeric kVA/consumer, 0 to 1,000,000; supported rate input | No category-specific rate in MDBs; aggregate ratios include about 3, 3.8667, 4 and 5 | Load Research / Commercial / System Planning |  | Conditional: category_rates mode requires a rate for every category, including LC. Aggregate historical ratios are not an approved rate schedule. [EC]
50 | LC lagging power factor | Provide the approved factor used to calculate kW and kvar from the category apparent-demand estimate. | Numeric factor greater than 0 and at most 1; lagging model in current automatic method | No usable value: reference positive kVA has zero kW and kvar | Load Research / Metering / System Planning |  | Conditional: category_rates requires PF for LC. Signed measured kvar or another allocation method uses the verified-demand workflow. [EC, NV]
51 | SI demand rate (1-phase industrial) | Provide the approved per-customer apparent-demand rate used to convert the verified category count into estimated demand. | Numeric kVA/consumer, 0 to 1,000,000; supported rate input | No category-specific rate in MDBs; aggregate ratios include about 3, 3.8667, 4 and 5 | Load Research / Commercial / System Planning |  | Conditional: category_rates mode requires a rate for every category, including SI. Aggregate historical ratios are not an approved rate schedule. [EC]
52 | SI lagging power factor | Provide the approved factor used to calculate kW and kvar from the category apparent-demand estimate. | Numeric factor greater than 0 and at most 1; lagging model in current automatic method | No usable value: reference positive kVA has zero kW and kvar | Load Research / Metering / System Planning |  | Conditional: category_rates requires PF for SI. Signed measured kvar or another allocation method uses the verified-demand workflow. [EC, NV]
53 | LI demand rate (3-phase industrial) | Provide the approved per-customer apparent-demand rate used to convert the verified category count into estimated demand. | Numeric kVA/consumer, 0 to 1,000,000; supported rate input | No category-specific rate in MDBs; aggregate ratios include about 3, 3.8667, 4 and 5 | Load Research / Commercial / System Planning |  | Conditional: category_rates mode requires a rate for every category, including LI. Aggregate historical ratios are not an approved rate schedule. [EC]
54 | LI lagging power factor | Provide the approved factor used to calculate kW and kvar from the category apparent-demand estimate. | Numeric factor greater than 0 and at most 1; lagging model in current automatic method | No usable value: reference positive kVA has zero kW and kvar | Load Research / Metering / System Planning |  | Conditional: category_rates requires PF for LI. Signed measured kvar or another allocation method uses the verified-demand workflow. [EC, NV]
55 | PB demand rate (public buildings) | Provide the approved per-customer apparent-demand rate used to convert the verified category count into estimated demand. | Numeric kVA/consumer, 0 to 1,000,000; supported rate input | No category-specific rate in MDBs; aggregate ratios include about 3, 3.8667, 4 and 5 | Load Research / Commercial / System Planning |  | Conditional: category_rates mode requires a rate for every category, including PB. Aggregate historical ratios are not an approved rate schedule. [EC]
56 | PB lagging power factor | Provide the approved factor used to calculate kW and kvar from the category apparent-demand estimate. | Numeric factor greater than 0 and at most 1; lagging model in current automatic method | No usable value: reference positive kVA has zero kW and kvar | Load Research / Metering / System Planning |  | Conditional: category_rates requires PF for PB. Signed measured kvar or another allocation method uses the verified-demand workflow. [EC, NV]
57 | AG demand rate (agriculture) | Provide the approved per-customer apparent-demand rate used to convert the verified category count into estimated demand. | Numeric kVA/consumer, 0 to 1,000,000; supported rate input | No category-specific rate in MDBs; aggregate ratios include about 3, 3.8667, 4 and 5 | Load Research / Commercial / System Planning |  | Conditional: category_rates mode requires a rate for every category, including AG. Aggregate historical ratios are not an approved rate schedule. [EC]
58 | AG lagging power factor | Provide the approved factor used to calculate kW and kvar from the category apparent-demand estimate. | Numeric factor greater than 0 and at most 1; lagging model in current automatic method | No usable value: reference positive kVA has zero kW and kvar | Load Research / Metering / System Planning |  | Conditional: category_rates requires PF for AG. Signed measured kvar or another allocation method uses the verified-demand workflow. [EC, NV]
59 | ST demand rate (street lights) | Provide the approved per-customer apparent-demand rate used to convert the verified category count into estimated demand. | Numeric kVA/consumer, 0 to 1,000,000; supported rate input | No category-specific rate in MDBs; aggregate ratios include about 3, 3.8667, 4 and 5 | Load Research / Commercial / System Planning |  | Conditional: category_rates mode requires a rate for every category, including ST. Aggregate historical ratios are not an approved rate schedule. [EC]
60 | ST lagging power factor | Provide the approved factor used to calculate kW and kvar from the category apparent-demand estimate. | Numeric factor greater than 0 and at most 1; lagging model in current automatic method | No usable value: reference positive kVA has zero kW and kvar | Load Research / Metering / System Planning |  | Conditional: category_rates requires PF for ST. Signed measured kvar or another allocation method uses the verified-demand workflow. [EC, NV]
H. Verified phase demands (only when manual demand is selected)
61 | R-phase customers by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Nonnegative whole integer; total equals verified category count | References often use fractional equivalents; these do not satisfy the current integer allocation rule | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
62 | Y-phase customers by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Nonnegative whole integer; total equals verified category count | References often use fractional equivalents; these do not satisfy the current integer allocation rule | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
63 | B-phase customers by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Nonnegative whole integer; total equals verified category count | References often use fractional equivalents; these do not satisfy the current integer allocation rule | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
64 | R-phase kW by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Finite nonnegative numeric kW | References record 0 even where kVA is positive; not a measured-demand basis | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
65 | Y-phase kW by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Finite nonnegative numeric kW | References record 0 even where kVA is positive; not a measured-demand basis | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
66 | B-phase kW by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Finite nonnegative numeric kW | References record 0 even where kVA is positive; not a measured-demand basis | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
67 | R-phase kvar by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Finite numeric kvar; signed values allowed with approval | References record 0 even where kVA is positive; not a measured-demand basis | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
68 | Y-phase kvar by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Finite numeric kvar; signed values allowed with approval | References record 0 even where kVA is positive; not a measured-demand basis | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
69 | B-phase kvar by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Finite numeric kvar; signed values allowed with approval | References record 0 even where kVA is positive; not a measured-demand basis | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
70 | R-phase kVA by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Finite nonnegative numeric kVA | Not established for the current project | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
71 | Y-phase kVA by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Finite nonnegative numeric kVA | Not established for the current project | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
72 | B-phase kVA by section / category | Provide the verified connected-phase demand schedule. Link each value to its current section, consumer category and measurement/estimation evidence. | Finite nonnegative numeric kVA | Not established for the current project | Metering / Load Research / System Planning |  | Conditional: manual demand, positive consumer counts and the indicated active phase. Inactive phases cannot carry nonzero loads. Check kW/kvar/kVA consistency. [NV, EPB]
I. Transformer model, connection and impedance options
73 | Nominal-voltage mode interpretation | Confirm the receiving SynerGEE meaning of the nominal-voltage mode and ensure its value is consistent with the LT form field and library. | Supported NomKvMode code; verified voltage basis | Reference: NomKvMode=C, SpecNomKv=4.16 | Transformer Engineering / SynerGEE Administrator |  | Conditional model semantic review. Do not label C as a particular calculation mode without vendor/library confirmation. [MDB, EC]
74 | Instance transformer percent impedance | Supply tested/approved impedance when choosing explicit instance impedance instead of the library. | PercentImpedance: positive numeric percent; declare rating/base | Reference value 0 with UseInstanceImpedance=0 is not a usable instance value | Transformer Testing / Transformer Engineering |  | Conditional mandatory when UseInstanceImpedance=1. Otherwise verified library impedance applies. [EC, EPB]
75 | Instance transformer percent resistance | Supply resistance on the same declared transformer base as the instance impedance. | PercentResistance: nonnegative numeric percent; same base as impedance | Reference value 0 with library mode enabled; no tested resistance recovered | Transformer Testing / Transformer Engineering |  | Conditional mandatory when UseInstanceImpedance=1; do not infer resistance from transformer make or capacity alone. [EC, EPB]
76 | High-side transformer winding connection | Confirm the winding connection used by the selected transformer model and its relationship to the actual circuit. | Exact supported HighSideConnectionCode code | Both references use YG on high and low sides | Transformer Engineering / Asset Records |  | Conditional on selected transformer representation. Recorded codes are available but not current-project nameplate evidence; not a separate universal form gate. [MDB]
77 | Low-side transformer winding connection | Confirm the winding connection used by the selected transformer model and its relationship to the actual circuit. | Exact supported LowSideConnectionCode code | Both references use YG on high and low sides | Transformer Engineering / Asset Records |  | Conditional on selected transformer representation. Recorded codes are available but not current-project nameplate evidence; not a separate universal form gate. [MDB]
78 | Transformer side orientation on the source section | Confirm which section end represents each winding side so voltage transformation follows the intended topology. | HighSideNearFromNode / NearFromNode supported flags | Reference: HighSideNearFromNode=1; NearFromNode=0 | Network Studies / Transformer Engineering |  | Conditional model confirmation. Do not copy orientation onto reversed or different current source wiring. [MDB, EPB]
79 | High-side grounding resistance and reactance | Provide the actual grounding model if grounding/sequence studies or the selected transformer connection require explicit values. | Resistance/reactance in the installed model native units; basis confirmed | Recorded HighSideGroundingResistance=0 and Reactance=0 | Protection / Earthing Design / Transformer Engineering |  | Conditional on grounding study/model. Zero reference fields are not proof of measured earth resistance. Not an unconditional export gate. [MDB]
80 | Low-side grounding resistance and reactance | Provide the actual grounding model if grounding/sequence studies or the selected transformer connection require explicit values. | Resistance/reactance in the installed model native units; basis confirmed | Recorded LowSideGroundingResistance=0 and Reactance=0 | Protection / Earthing Design / Transformer Engineering |  | Conditional on grounding study/model. Zero reference fields are not proof of measured earth resistance. Not an unconditional export gate. [MDB]
81 | Transformer tap setting | Confirm the transformer tap represented by the model rather than copying a historic instance. | Supported TapSetting numeric value; meaning/basis from receiving library | Reference TapSetting=1 | Distribution Operations / Transformer Engineering |  | Conditional on transformer/tap representation. Not a substitute for nameplate tap position or approved voltage regulation settings. [MDB]
82 | LC category interpretation and connection policy | Confirm the LC tariff/classification and how its demand is represented; retain the recorded category until reviewed. | Written category definition and approved rate or measured-demand mapping | Application label: Commercial (LC; confirm classification) | Commercial / Load Research |  | Conditional when LC data are modeled. No automatic reclassification or inferred phase count from the label. [LOOKUP, EC]
J. PV and annual generator modeling (only for included PV)
83 | PV inclusion or approved exclusion decision | Decide whether each positive PV record is represented by the supported generator mapping or covered by an explicit engineering-approved exclusion. | v2 generator mapping, or pv_exclusion reason with authorized review | One Kot Madina reference contains a generator; PDF PV fields do not establish a model policy | Distributed Generation / System Planning |  | Conditional on positive PV capacity. Omitting it without an approved exclusion fails full validation. [NV, SM]
84 | PV-to-current-section association | Identify the actual section and PV observation belonging to each generator; resolve multiple PV records on one section. | pv_record_id and current section_id; one supported generator per section | Reference IDs belong to historical networks; current association not provided | DG / GIS / Survey Verification |  | Conditional on included PV. Current writer rejects duplicate generator mappings and does not arbitrarily aggregate several installations. [SM]
85 | Generator output percentage | Provide the generator output percentage under the approved operating scenario. | DGenOutputPct: finite numeric 0-100 percent | Component reference evidence includes DGenOutputPct=100 | DG / System Planning |  | Conditional mandatory for included full-mode generator; source component settings are not universal defaults. [SM, MDB]
86 | Generator voltage setpoint and unit basis | Confirm the generator setpoint and the voltage basis expected by the selected SynerGEE model. | DGenVoltSet: positive numeric in supported native model units; basis declared | Component reference evidence includes DGenVoltSet=120 | DG / Voltage Control / SynerGEE Administrator |  | Conditional mandatory for included full-mode generator. Do not interpret 120 as kV or LT voltage without confirming units. [SM, MDB]
87 | Generator study-year numbering and base-year meaning | Define modeled year indices and their actual calendar/scenario meaning; include the required base year. | Unique nonnegative YearNumber integers; base index 0 required | Historical SAI model years 2015-2025; not the current study schedule | System Planning / DG |  | Conditional on annual PV modeling. Current mapping requires a base-year (0) record but does not infer current calendar labels. [SM]
88 | Annual generator capacity factor | Provide the scenario/year capacity factor used for each generator annual record. | Finite CapacityFactor from 0 to 1, for each modeled year | Reference component evidence available; current annual scenario not approved | DG / Renewable Planning |  | Conditional mandatory for each full-mode generator-year record. Do not derive from installed kW alone. [SM]
89 | Generator R-phase kW for every modeled year | Provide the generator output for the indicated connected phase, with the scenario and year recorded. | Finite nonnegative kW | Historical generator outputs are instance/year-specific, not reusable current values | DG / Metering / Network Studies |  | Conditional mandatory for this active generator phase. Inactive phases must be NULL or zero; no automatic split of installed PV capacity. [SM]
90 | Generator Y-phase kW for every modeled year | Provide the generator output for the indicated connected phase, with the scenario and year recorded. | Finite nonnegative kW | Historical generator outputs are instance/year-specific, not reusable current values | DG / Metering / Network Studies |  | Conditional mandatory for this active generator phase. Inactive phases must be NULL or zero; no automatic split of installed PV capacity. [SM]
91 | Generator B-phase kW for every modeled year | Provide the generator output for the indicated connected phase, with the scenario and year recorded. | Finite nonnegative kW | Historical generator outputs are instance/year-specific, not reusable current values | DG / Metering / Network Studies |  | Conditional mandatory for this active generator phase. Inactive phases must be NULL or zero; no automatic split of installed PV capacity. [SM]
92 | Generator R-phase kvar for every modeled year | Provide the generator output for the indicated connected phase, with the scenario and year recorded. | Finite numeric kvar; signed values allowed | Historical generator outputs are instance/year-specific, not reusable current values | DG / Metering / Network Studies |  | Conditional mandatory for this active generator phase. Inactive phases must be NULL or zero; no automatic split of installed PV capacity. [SM]
93 | Generator Y-phase kvar for every modeled year | Provide the generator output for the indicated connected phase, with the scenario and year recorded. | Finite numeric kvar; signed values allowed | Historical generator outputs are instance/year-specific, not reusable current values | DG / Metering / Network Studies |  | Conditional mandatory for this active generator phase. Inactive phases must be NULL or zero; no automatic split of installed PV capacity. [SM]
94 | Generator B-phase kvar for every modeled year | Provide the generator output for the indicated connected phase, with the scenario and year recorded. | Finite numeric kvar; signed values allowed | Historical generator outputs are instance/year-specific, not reusable current values | DG / Metering / Network Studies |  | Conditional mandatory for this active generator phase. Inactive phases must be NULL or zero; no automatic split of installed PV capacity. [SM]
95 | Meter-point section association | Choose where a meter point is attached if meter records are required in the intended study. | Exactly one source_section or survey_section_id per meter; one meter per section | All nine references have a meter row with only SectionId populated | Metering / GIS / Network Studies |  | Conditional on adding meters. Blank readings in references are not a requirement to invent measurements. [SM, MDB]

## Optional
Engineering Configuration Data Requirement Sheet — Optional
HAZECO. Reviewed 19 October 2026. 21 items. Additional study/model settings; not universal blockers in the current generator.
Fill the amber Actual Value column only. Reference examples require departmental confirmation. Source keys are explained on Evidence and Scope.
Sr. No. | Parameter / Configuration Name | Purpose / Technical Description | Required Format / Unit | Sample / Possible Value | Source / Responsible Department | Actual Value (To Be Filled) | Remarks / Priority
K. Optional supply, voltage-control and study settings
96 | Projection WKT or alternate projection reference | Provide additional CRS definition text only if required by the receiving installation or document standard. | Optional projection_wkt text, form maximum 255 characters | Reference ProjectionWKT is an empty string | GIS / SynerGEE Administrator |  | Optional. The form accepts blank; do not truncate an external WKT to fit. EPSG/name confirmation remains mandatory. [EC, MDB]
97 | Operating feeder bus voltage | Specify the operating source voltage for a study when it differs from nominal voltage. | BusVoltageLevel in supported SynerGEE voltage basis | Reference BusVoltageLevel=11.37; nominal feeder voltage=11 | System Operations / System Planning |  | Optional study value, not the form nominal-voltage field. Confirm units and scenario before reuse. [MDB]
98 | Per-phase source voltage levels and angles | Provide explicit unbalanced source conditions when the study enables per-phase voltage control. | UseByPhVoltLevel plus ByPhVoltLevelPh1/2/3 and ByPhVoltDegPh1/2/3 | Reference flag=0; levels=11; angles=0, -120, +120 | System Operations / Network Studies |  | Optional unless the chosen study enables this source model; stored disabled values are not measurements. [MDB]
99 | Source positive-sequence impedance | Provide source resistance/reactance when fault level or source-drop modeling requires finite source impedance. | PosSequenceResistance / PosSequenceReactance; native units and voltage base declared | Both reference fields=0; no measured/calculated source impedance established | Grid System Studies / Protection |  | Optional for current export gate; required only by a selected study/model. Zero is not a fault-level assessment. [MDB]
100 | Source zero-sequence and line-to-ground fault resistance | Provide the source grounding/sequence inputs for a selected unbalanced-fault study. | ZeroSequenceResistance / Reactance; LineToGroundFaultResistance; native units/base | Reference sequence/fault resistance fields=0 | Protection / Earthing Studies |  | Optional study-specific group; not a mandatory extra requirement for every generated MDB. [MDB]
101 | Feeder demand scaling and aggregate demand values | Confirm any feeder-wide scaling or aggregate demand inputs used by the receiving study. | FeederMultiplier; phase demand / PF fields in native model units | Reference FeederMultiplier=1; feeder demand/PF fields=0 | Load Research / Network Studies |  | Optional. Aggregate feeder zero PF is not an acceptable category-rate power factor. [MDB]
102 | Distributed-load ZIP model settings | Confirm distributed-load constant impedance/current percentages if the study uses the source load-model fields. | PercentDistLoadConstImpedance / Current in percent; remaining model basis confirmed | Reference fields: 40 / 10 | System Planning / Load Research |  | Optional model-design confirmation; these fields are not independent mandatory entries in the current form. [MDB]
103 | Spot-load ZIP model settings | Confirm spot-load constant impedance/current percentages if spot loads are selected. | PercentSpotLoadConstImpedance / Current in percent | Reference fields: 40 / 30 | System Planning / Load Research |  | Optional / selected-load-model specific. Do not assume every customer is a spot load. [MDB]
104 | Spot/distributed load mode and load placement | Confirm the load representation and location convention for the selected study. | IsSpotLoad; LocationToModelSpotLoads supported code; CapacityFactor | Reference: IsSpotLoad=0; location=C; CapacityFactor=1 | System Planning / Load Research |  | Optional mapping confirmation. These are available historical conventions, not an approved current demand method. [MDB]
105 | Demand coincidence / diversity study basis | Document any diversity/coincidence assumption included in the approved demand estimation standard. | Written method and factors only if that method calls for them | Not provided as a verified category method in the inputs | Load Research / Commercial |  | Optional method-specific evidence. No separate universal diversity-factor field is required by this application. [EC]
106 | Load growth model and horizon | Provide growth curves/rates and forecast years if a future-year load study is requested. | PercentLoadGrowthRate / growth-curve references / reviewed study years | Section reference growth rate=2; source historic labels 2015-2025 | System Planning / Forecasting |  | Optional forecast scope. Historical years and rate are not current approvals. [MDB]
107 | Section ampacity override and emergency rating | Supply explicit section/equipment rating overrides only if the selected model uses them rather than the installed library. | UseSectAmpRating flag; AmpRating / emergency ratings in native model units | Section reference: UseSectAmpRating=0; AmpRating=100 | Distribution Design / Asset Ratings |  | Optional override. The disabled 100 value does not establish a real 100 A conductor rating. [MDB]
108 | Neutral grounding and load phase-ground convention | Confirm grounding/load connection fields when implementing the applicable circuit model. | NeutIsGrounded; role-specific LoadConnectionPhaseGnd codes | Reference: NeutIsGrounded=1; supply phase-ground=0, downstream=1 | Distribution Design / Earthing / Network Studies |  | Optional explicit model confirmation, not a new form gate. The two phase-ground values must not be flattened to one global value. [MDB]
109 | Tap-control / LTC operating settings | Provide regulation controls only if the selected transformer/control model uses LTC behavior. | Supported gang/manual flags, per-phase tap/voltage/band settings and tap limits | Reference forward settings=122; band=0.75; limits +6/-4; units/meaning require confirmation | Transformer Engineering / Voltage Control |  | Optional control-study scope. These historical fields do not prove LTC is installed or active. [MDB]
110 | Transformer network protection state | Confirm network-protector flags if a modeled transformer has that function. | NetProtEnabled / NetProtIsAuto / NetProtIsOpen supported flags | Reference flags: 0 / 0 / 0 | Protection / Distribution Operations |  | Optional equipment-specific scope; not a universal final-export blocker. [MDB]
111 | Meter readings, meter type and calibration settings | Provide meter data only when the study uses a modeled meter for demand, ratings or reliability calibration. | Selected meter fields and native units; supported type/mode codes | Reference meter records contain SectionId only; remaining fields NULL | Metering / Network Studies |  | Optional measurements. Section attachment becomes conditional if a meter is added; no readings are inferred from NULL. [SM, MDB]
112 | Reliability failure, repair and cost assumptions | Provide approved reliability inputs only if a reliability/economic study is part of the modeled scope. | Failure rates per year; repair times hours; cost currency/basis declared | Reference transformer repair time=6 h; repair cost=5000 in source monetary units | Asset Management / Reliability / Finance |  | Optional study-specific values. Source zeros/defaults are not verified reliability statistics. [MDB]
113 | Equipment energization and retirement model years | Define year indices when the model uses equipment commissioning/retirement scenarios. | Supported EnergizeYear / RetireYear model indices and study-year schedule | Reference values: 0 and 100 | Asset Management / System Planning |  | Optional. These are model indices, not established physical commissioning/retirement calendar dates. [MDB]
114 | Protection, switching, regulation and capacitor studies | Provide equipment libraries, settings and topology only if these additional devices/studies are requested. | Vendor-supported device records/settings and a separately reviewed supported mapping | Relevant reference tables are empty; current writer does not populate these device tables | Protection / System Planning / Software Team |  | Optional additional scope. Current v1/v2 writer supports six/nine tables; this may need implementation beyond supplying data. [WR, MDB]
115 | Consolidated multi-transformer feeder export decision | Confirm common-source identities and explicit support if exporting more than one transformer in a single MDB. | consolidated_supported=true only with reviewed consistent source/network mapping | No current-project consolidated feeder design inferred from individual MDBs | Network Studies / GIS / Application Admin |  | Optional project-specific scope. Full export rejects an unapproved consolidated mapping. [EPB]
116 | Model-specific temperature / rating / earth-return assumptions | Supply additional physical assumptions only where the installed conductor/configuration model requires them. | Native library model parameters and documented bases; no universal numeric defaults | Not established by the reference ID strings or GPX metadata | Distribution Design / Library Custodian |  | Optional/model-dependent beyond the installed package. Do not turn absent generic parameters into universal application requirements. [MDB]

## Evidence and Scope
Scope, classification and source evidence
HAZECO. Engineering Configuration Data Requirement Sheet. Read-only assessment dated 19 October 2026.
Evidence below documents availability and limits. It is not an engineering approval or a list of values already accepted for this project.
Evidence type | Source / subject | Observed information | Limit / interpretation
Scope | Purpose | Engineering Department requirement sheet for full engineering validation and a usable supported SynerGEE model. All Actual Value cells are deliberately empty. | No application code, database or configuration was changed.
Scope | Classification | Mandatory = full-mode form/export gate or required current-source mapping. Conditional = required only under the stated method/device/data condition. Optional = study-specific, not a universal current gate. | Simple MDB Generation can allow NULL engineering fields; that is not evidence of a complete electrical model.
Scope | How to respond | Fill only the amber Actual Value cells, or cite an attached approved library/data schedule where the parameter is a package or per-section schedule. | Suggested department functions are proposed owners; HAZECO should assign the named approving officers.
Scope | Data versus approval | Known reference values are examples requiring current-project confirmation. Missing values are explicitly identified; no sample implies engineering approval. | Form choice requirements are distinguished from optional model fields.
Scope | Coverage limitation | Five unique PDFs (75 pages) reviewed for field content/layout; representative headers/legends inspected. Five unique GPX files contain 539 waypoints. No complete handwriting transcription was performed. | This is a configuration gap assessment, not a certification that every survey row is complete.
Scope | Reference scope | Nine unique engineering MDBs: seven latest named files plus both Industrial models; Mosa Pak counted once. | Intermediate Field_Data / GPS_Points Data Entry MDBs are not final SynerGEE design libraries.
Available | Canonical MDB structure | All nine engineering files match 50 tables, 1,065 fields, 133 indexes and 41 relationships. | Schema availability does not establish the correctness of the electrical design.
Available | Common engineering evidence | 133 common observed parameters and eight conflicts are recorded in resources/mdb/engineering-defaults.json. | Physical equipment definitions, installed revisions and project approval are not embedded.
Available | Frequency / nominal supply | All nine source models: Frequency=60; InstFeeders.NominalKvll=11; BusVoltageLevel=11.37. | Keep operating voltage separate from nominal voltage; obtain project approval.
Available | Transformer references | Type labels: 50 KVA, 100 KVA, 200 KVA; high/low connection codes YG/YG; UseInstanceImpedance=0. | Numeric zero impedance fields do not establish physical zero impedance.
Available | Conductors / construction | ANT, DOG, GNAT, WASP, INSULATED ANT plus four leading-space families; configuration ID 12.5/7.2 kV cross arm C2-2. | Review exact ID matching and the secondary link neutral omission.
Available | Survey PDF fields | Headers, kVA/make/mounting/service details, S/E identity, R/Y/B/N marks, equipment/pole observations, consumer counts and some PV references/capacity/remarks. | These do not establish CRS, installed electrical library revisions, transformer test data, or approved demand rates/PF.
Available | GPX content | Coordinates, elevations, waypoint names, times and descriptive/extension metadata. | GPX does not establish electrical conductor models, circuit connectivity, winding properties or demand assumptions.
Conflict GEO | Actual cross-check | A1408.gpx waypoint 591: lat 30.3701350093, lon 71.8793389667; IndustrialT-4060116233 Node 1140825591: X 776727, Y 3363318. | Only the named cross-check is asserted; no automatic rebinding or project CRS change was made.
Conflict GEO | Projection comparison | EPSG:32642 projection of that GPX point differs from the MDB node by 0.4619 m. EPSG:32643 differs by 576657.6634 m. | MDB ProjectionFile says WGS 1984 UTM Zone 43N. GIS must resolve the conflict; an EPSG derived from the label is not validated.
Conflict | Demand evidence | 350 positive-customer phase records; 341 at approximately 3 kVA/customer; others approximately 3.8667, 4 and 5. All positive-kVA phases have zero kW and kvar. | Do not adopt a universal 3 kVA/customer rate or derive a usable PF from these inconsistent model records.
Available | Supported export scope | v1: SAI_Control, Node, InstFeeders, InstSection, InstPrimaryTransformers, Loads. v2 also supports InstMeterPoints, InstDGens and InstMymDGens. | Other schema tables are not automatically modeled. Protection/capacitor/regulator data are additional scope, not universal missing inputs.
Available | Automatic / already supplied data | The application computes export IDs, hashes, timestamps, phase strings and projected coordinates after approved inputs are supplied. PDF/GPX supply most observation identities and counts. | These are not additional departmental numerical requirements. Ambiguities still need verification.
Scope | Legacy builder distinction | The older transformer workspace requires category_rates and WGS84 northern UTM under full mode; positive PV uses the current MDB Creation & Verification workflow. | Manual phase-demand and v2 device requirements apply to the current workflow when selected.
Code / evidence | EC | app/Services/Mdb/EngineeringConfiguration.php | save() validation, saveDraft(), approved(), apply(), demand()
Code / evidence | NV | app/Services/Mdb/NetworkValidator.php | validate(), validateSection() and demand/coordinate/PV checks
Code / evidence | EPB | app/Services/Mdb/ExportPayloadBuilder.php | build(), load(), validateSection(), point()
Code / evidence | SM | app/Services/Mdb/SupplementalMapping.php | build(): meter/generator associations and annual outputs
Code / evidence | LOOKUP | app/Services/Mdb/EntryLookups.php | CONSUMERS, options(), libraryCode()
Code / evidence | UI | resources/views/engineering/edit.blade.php | Mandatory form fields and displayed units
Code / evidence | WR | scripts/mdb/export-reviewed-mdb.ps1; scripts/mdb/schema-contract.ps1 | Supported table sets, clean template, canonical schema and value checks
Code / evidence | GEO | outputs/engineering_requirements_20261019/geo_check.json | Read-only GPX/MDB projection comparison; PROJ calculation
Code / evidence | MDB | resources/mdb/engineering-defaults.json; output/engineering-defaults-review/ | Nine read-only source inspections and consolidated field evidence
Code / evidence | PDF / GPX | outputs/engineering_requirements_20261019/reviewed_source_inventory.json | Five PDF and five GPX content hashes and metadata; source paths below
Reference MDB | Allah AbadT-4130116282.mdb | SHA-256: 187ac736140f8ecfab9f831d95cb46a2e738525e197343e07b4795cd81e82845 | Full read-only schema/row inspection from the earlier consolidated analysis; source hashes verified again for this sheet.
Reference MDB | Allah AbadT-4130116284.mdb | SHA-256: ce6fe957962bd85057fb24f8d6558e4d377c0e375325bbef1071c121b2d4a7c0 | Full read-only schema/row inspection from the earlier consolidated analysis; source hashes verified again for this sheet.
Reference MDB | IndustrialT-4060116233.mdb | SHA-256: 4549ff4d5b29e7a2bde79ec3295aff3396af45709bce062ef1c47e30c1de3262 | Full read-only schema/row inspection from the earlier consolidated analysis; source hashes verified again for this sheet.
Reference MDB | IndustrialT-4120623648.mdb | SHA-256: 7e9dd3ff99722fc74170513d774fb769d6b8a2bfde4c9c2b06b15f9ab956368e | Full read-only schema/row inspection from the earlier consolidated analysis; source hashes verified again for this sheet.
Reference MDB | Kot MadinaT-8160421110.mdb | SHA-256: eba5711b1c633c48839146bb42ed9ebec6cbe7d6028a81f77cb6345d69a995fd | Full read-only schema/row inspection from the earlier consolidated analysis; source hashes verified again for this sheet.
Reference MDB | Kot MadinaT-8160421145.mdb | SHA-256: 1065f140ba2c964c1fb30d4e0e73aa581db03913b5e0ca90f3b1bae5c731bf3a | Full read-only schema/row inspection from the earlier consolidated analysis; source hashes verified again for this sheet.
Reference MDB | Mosa PakT-2241017145.mdb | SHA-256: f1c885148452de3bc0be5d02b329f82cd32a6b8053ef69d1c45a65b0d20e6035 | Full read-only schema/row inspection from the earlier consolidated analysis; source hashes verified again for this sheet.
Reference MDB | New BosanT-2211117034.mdb | SHA-256: 52b87163f6fefceaa1eb60571ef0803984ac5c4e545777823f454208e0cafd38 | Full read-only schema/row inspection from the earlier consolidated analysis; source hashes verified again for this sheet.
Reference MDB | Z TownT-2301017107.mdb | SHA-256: 43570810f75671ac3cf9ff94f2780345edc050452d21467b442b92cbbd24bcf5 | Full read-only schema/row inspection from the earlier consolidated analysis; source hashes verified again for this sheet.
Survey source | A0808.gpx | SHA-256: ed0055525e5a7aaa3fa66dc7266e9b1169099dbb48183dfea6b56d17cea9dbb0 | 62 waypoints; duplicate uploaded copies are counted once.
Survey source | A0808.pdf | SHA-256: e97216a7e849f3f4d3291bd4397d184984f916aa76cd594cfa56e49eae4d0e0c | 10 pages; duplicate uploaded copies are counted once.
Survey source | A1308.gpx | SHA-256: 1488392706bb07161f0ca2813060163e25cac0f3cbe552f88e0237b9af851982 | 86 waypoints; duplicate uploaded copies are counted once.
Survey source | A1308.pdf | SHA-256: 718593b9597f6a16f18fe046ad87db091419b6b2e851810c1c224778964b0663 | 14 pages; duplicate uploaded copies are counted once.
Survey source | A1408.gpx | SHA-256: c30e940261fa1eaa5c418355ee7117d6710b40dc9b03dc02247b47c8f5188709 | 54 waypoints; duplicate uploaded copies are counted once.
Survey source | A1408.pdf | SHA-256: 394ee22bee502fa6f05a39834121b8790a7272a312ab8d9d4c8a6735aa7cba50 | 9 pages; duplicate uploaded copies are counted once.
Survey source | storage\app\private\mdb-workflow\sources\1\060a8d3f-a801-44f4-99d0-660820c87773.gpx | SHA-256: 59f376830b3119a81f3f79cd607abc1cc71798ea4d8ff147c3b0ac1f3fde1fe6 | 120 waypoints; duplicate uploaded copies are counted once.
Survey source | storage\app\private\mdb-workflow\sources\1\0c1896c6-9ada-43ee-b302-c7ec36d3dae9.pdf | SHA-256: 170b782cb55a9923e4590b5dcc3a46e30224ce4f0d5ccfc317b800a637c9f969 | 14 pages; duplicate uploaded copies are counted once.
Survey source | storage\app\private\mdb-workflow\sources\15\00a32a0c-3b67-4db2-b8fb-c3274dcfe205.gpx | SHA-256: 46c4de155a6e137187b3b66d1d30962dda1a7c4ffd9fb50d4d17f2f6039f9b6f | 217 waypoints; duplicate uploaded copies are counted once.
Survey source | storage\app\private\mdb-workflow\sources\15\5caa2b3b-0d4e-49ab-95fb-598d5d42bca9.pdf | SHA-256: f47ea2f9a55bd7b076fa3a43445f8b6a91f3893534f6abce0373a111272dee52 | 28 pages; duplicate uploaded copies are counted once.
Code hash | app/Services/Mdb/EngineeringConfiguration.php | SHA-256: 5a02b274743a97212ba654ab1dcc73adb40d01340a9bd85395864cac7299adf2 | Read-only application version inspected for this requirement assessment.
Code hash | app/Services/Mdb/NetworkValidator.php | SHA-256: 75d244b9eb9ca6d40e6edff6ce0d97d31da4383b92396efd9368a1f202d46725 | Read-only application version inspected for this requirement assessment.
Code hash | app/Services/Mdb/ExportPayloadBuilder.php | SHA-256: af31a8bbb204676d7d29f647c173f461b6b1148c9e64654810a4c448533a21fa | Read-only application version inspected for this requirement assessment.
Code hash | app/Services/Mdb/SupplementalMapping.php | SHA-256: c538161ef85fa2b5cf0d13e519dae6ac672a1f8b90454c7a6a74df5369b274b0 | Read-only application version inspected for this requirement assessment.
Code hash | app/Services/TransformerMdbNetworkService.php | SHA-256: 754964ff7c92675979bb1c74936e7bd26d50d22dae1fabf6c85916d172143c0f | Read-only application version inspected for this requirement assessment.
Code hash | app/Services/Mdb/EntryLookups.php | SHA-256: 99b4746258c95686a857fae8a90b80877ce01976a336598d11bb6b71cfa7e2e2 | Read-only application version inspected for this requirement assessment.
Code hash | app/Services/Mdb/GenerationMode.php | SHA-256: 4f751ca2c40b91b334dc9fa3ae988ec06f5b8a9658e1d9d26ba635744f2db107 | Read-only application version inspected for this requirement assessment.
Code hash | scripts/mdb/export-reviewed-mdb.ps1 | SHA-256: 45a6c3f8bc2498fe7a2f402878dd9c68b497d1e650ff4c38f91867575f301175 | Read-only application version inspected for this requirement assessment.
Code hash | scripts/mdb/schema-contract.ps1 | SHA-256: 2b77c031163a338a6f2c84c3919cf406d86314b3827d37faeac110d2792f46d6 | Read-only application version inspected for this requirement assessment.
Code hash | resources/views/engineering/edit.blade.php | SHA-256: e543c7b81ff67aeae15678ec518ee33097d55c0b87c0cb4beb82466e73a6a90c | Read-only application version inspected for this requirement assessment.